## Read Me
SETTY-5.3 Estimator ®
COVID 19 Airborne Transmission Infection Rate Estimator
Developed by: | Raj Setty, P.E., LEED AP, CxA, ASHRAE SCHOOLS EPIDEMIC TASK FORCE MEMBER
SETTY Consulting Engineers
Contributors: | Adarsha BV, Rakshith Kumar R
Version & Date | V5.3 | February 10, 2023
About this calculator:
This calculator consists of 3 sections:
Read Me: | The intent of the estimator is to model different filtration, outdoor air, occupancy rates, exposure times, disinfection and air change rates to give a predicted probability of cross infections within a closed setting. Increasing filtration levels, limiting occupancy, reducing exposure time, increasing outside air and including disinfection will all reduce the viral transmission rate.
Estimator: | The probability of infection has been calculated using the Gammaitoni and Nucci (1997a) version of the Wells-Riley Equation which is defined by factors for airborne disease transmission. As scientists have established the viability of COVID-19 in the airstream, the shift to actualization of strategies to reduce the risk of transmission falls to HVAC professional engineers. Those engineers who are following ASHRAE guidelines will be best positioned to help solve the challenges of re-opening buildings. For planning, budgeting and modeling engineering solutions, the estimator has been created as a pre-step to operational, design and construction solutions.
The estimator's baseline conditions should be entered based on field specific condition which establishes your current risk of transmission if your building re-opened as is. This baseline is the most important step in accurate prediction for the risk of transmission. Several proposed scenarios are available for the user to adjust and help predict what factors in conjunction with each other help to reduce the probability of future infections.
Source: | This source section contains the list of references used to build this calculator.
Background / Context
ASHRAE Statement on operation of heating, ventilating, and air-conditioning systems to reduce SARS-CoV-2 transmission
Ventilation and filtration provided by heating, ventilating, and air-conditioning systems can reduce the airborne
concentration of SARS-CoV-2 and thus the thermal stress to people that may be directly life threatening and that may also
lower resistance to infection. In general, disabling of heating, ventilating, and air-conditioning systems is not a
recommended measure to reduce the transmission of the virus.
Disclaimer
While there are no 100% solutions to ensure no one will be infected by a virus in a common space like a classroom, there are operational and HVAC system changes that will reduce the airborne concentration of viruses. Buildings will re-open and HVAC changes must be implemented as part of the viral load reduction strategies. The underlying directive for HVAC engineers is to "Do No Harm". The application of better filtration, reduction in exposure time, reduction in occupancy, more fresh air to the building spaces and disinfection of the airstream via UV-C all have positive impacts to the indoor air quality. While there are cost implications to the various applications, the risk of negatively impacting the indoor air quality is almost negligible.

## Estimator
SETTY-5.3 Estimator ®
Small Space Airborne Transmission Infection Rate Estimator (Using Wells-Riley model)
| BUILDING SPACE AND HVAC UNIT VARIABLES | [14 empty] | User Input
|  | Baseline Case | Scenario - 1 (Building Changes) | Scenario - 2 | Scenario - 3 | Remarks / Reference | [9 empty] | Calculated Output
Room Area, A (Sq. ft.) = |  | 1500 | 1500 | 1500 | 1500 | User Defined (max 2000 sf) & not applicable for non-educational facilities | Override | 1 | [7 empty] | Calculated, but User can override
Room Height, H (ft) = |  | 9 | 9 | 9 | 9 | User Defined (Floor to Ceiling) - Site specific | ASHRAE 62.1 | N/A | [7 empty] | Calculated Output
Room Volume, V (cu. ft) = |  | 13500 | 13500 | 13500 | 13500 | Calculated
If Ventilation unknown, select category per code ASHRAE 62.1 = |  | Classroom, pre-K | Classroom, pre-K | Classroom, pre-K (10% higher OA) | Classroom, pre-K (10% higher OA) | User Defined, ASHRAE 62.1-2019 (Table 6-1) | IF STATEMENT | 0 |  | Person | Pulmonary | Quanta | Activity
Ventilation per person per ASHRAE 62.1, (CFM) = |  | N/A | N/A | N/A | N/A | Calculation Factor - code minimum, ASHRAE 62.1-2019 (Table 6-1) | Pulmonary ventilation rate of a person, ps (CFM)
If Ventilation known, Enter CFM Airflow |  | 500 | 500 | 500 | 500 | User Defined, Can not exceed Total CFM |  |  |  | Child, U14 | 0.29 | 65 | Resting, Loudly speaking
[10 empty] | Teen | 0.32 | 135 | Standing, Loudly speaking
Total Room Airflow, Q (TA = RA+OA) (CFM) = |  | 2000 | 2000 | 2000 | 2000 | User Defined - space specific |  |  |  | Adult | 0.81 | 170 | Light Exercise, Loudly speaking
Total Room Air changes/rotations, (ACH) = |  | 8.8889 | 8.8889 | 8.8889 | 8.8889 | Calculated
Total Recirculation air volume, Q(RA) (CFM) = |  | 1500 | 1500 | 1500 | 1500 | Calculated - Building recirculated air volume
Total Recirculation air changes/rotations, (ACH) = |  | 6.6667 | 6.6667 | 6.6667 | 6.6667 | Calculated based on room volume and Q(RA)
Ventilation Airflow, Q(OA) (CFM) = |  | 500 | 500 | 500 | 500 | Calculated | Category | CFM/People | CFM.Area | Occupant Density/sf | Total Ventilation cfm
Ventilation Air changes/rotations, λventilation (ACH) = |  | 2.2222 | 2.2222 | 2.2222 | 2.2222 | Calculated |  |  |  |  | Baseline | Scenario 1 | Scenario 2 | Scenario 3
| OCCUPANT AND USAGE ADJUSTMENTS FOR INFECTION PROBABILITY | [5 empty] | No Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Infectors, I = |  | 1 | 1 | 1 | 1 | User Defined, Use (1) unless known quantity of infectors | Classroom, pre-K | 10 | 0.12 | 0.025 | 555 | 555 | 555 | 555
Infected Person, (Child, U14 / Teen / Adult) = |  | Child, U14 | Child, U14 | Child, U14 | Child, U14 | User Defined | Classroom, pre-K (10% higher OA) | 10 | 0.12 | 0.025 | 610.5 | 610.5 | 610.5 | 610.5
Number of Susceptibles in room, S = |  | 25 | 25 | 25 | 25 | User Defined - According to IES, NCES survey, Table 7 (ranges 22 - 26) | Classroom, high school | 10 | 0.12 | 0.035 | 705 | 705 | 705 | 705
Infectors & occupants share a space time, t (hr) = |  | 6 | 6 | 6 | 6 | User Defined - According to IES, NCES survey (ranges 6 - 8 hrs) | Classroom, high school (10% higher OA) | 10 | 0.12 | 0.035 | 775.5 | 775.5 | 775.5 | 775.5
Pulmonary ventilation rate of a person, ps (CFM) = |  | 0.29 | 0.29 | 0.29 | 0.29 | Calculation Factor - Ranges 0.29 to 1.94 cfm, From Buonnano et al. (2020) | Corridor | 0 | 0.06 | 0 | 90 | 90 | 90 | 90
Rate of Covid 19 production by occupant, qo (quanta/hr) = |  | 65 | 65 | 65 | 65 | Calculation Factor - Ranges 2 - 408 q/hr, From Buonnano et al. (2020) Infectious doses (quanta/hr): Activity assumed for 'Child, U14' = Resting, loudly speaking, 'Teen' = standing, loudly speaking and for 'Adult' = Light Exercise, loudly speaking (this is uncertain parameter and may vary). | Lobbies | 5 | 0.06 | 0.15 | 1215 | 1215 | 1215 | 1215
Rate of Covid 19 production for space total, qs (quanta/hr) = |  | 65 | 65 | 65 | 65 | Calculated | Office | 5 | 0.06 | 0.005 | 127.5 | 127.5 | 127.5 | 127.5
| INFECTIOUS PARTICLE VARIABLES | [5 empty] | Office (10% higher OA) | 5 | 0.06 | 0.005 | 140.25 | 140.25 | 140.25 | 140.25
Decay rate of the virus, Kinactivation (/hr) = |  | 0.35 | 0.35 | 0.35 | 0.35 | Calculation Factor Ranges 0 - 0.62 /hr, from Miller et al. (2020), Use 0.35 for a student | Conference | 5 | 0.06 | 0.05 | 465 | 465 | 465 | 465
Infectious particle deposition rate, Kdeposition (/hr) = |  | 0.3 | 0.3 | 0.3 | 0.3 | Calculation Factor Ranges 0.24 - 1.5/hr, from Miller et al. (2020) | Library | 5 | 0.12 | 0.01 | 255 | 255 | 255 | 255
UV-C Dose in Central HVAC system/ Ducted system (µ-watt-s/cm2) = |  | None | None | None | None | User Defined - UV-C dose (µ-watt-s/cm2) ranges from 1200 (50%) to 4000 (90%)* | Lecture Hall | 7.5 | 0.06 | 0.15 | 1777.5 | 1777.5 | 1777.5 | 1777.5
BUILDING HVAC INDOOR AIR QUALITY ADJUSTMENTS
Air filter MERV rating efficiency in HVAC system serving the space such as AHU, FCU, UV, FPVAV, HP etc. = |  | MERV 8 | MERV 8 | MERV 8 | MERV 13 | User Defined Filter efficiency based on particle size 0.1 µm.
Infectious particle removal rate by filtration, Kfiltration (/hr) = |  | 1.3354 | 1.3354 | 1.3354 | 3.6725 | Calculated | UVC Intensity (BUILDING) | [7 empty] | Run Time (hr)
Total loss rate, C (/hr) = |  | 4.2077 | 4.2077 | 4.2077 | 6.5447 | Calculated | None | 0 | [6 empty] | 0
[7 empty] | 1200 | 0.5 | [6 empty] | 1
Probability of infection, P(infection) |  | 10.85% | 10.85% | 10.85% | 7.216% | Calculated, Considering IAQ improvements only in HVAC Central System | 2000 | 0.7 | [6 empty] | 2
Probability of infection, P(persons) |  | 3 | 3 | 3 | 2 |  | 3000 | 0.8 | [6 empty] | 3
| PORTABLE & LOCAL AIR FILTRATION UNIT(S) INDOOR AIR QUALITY ADJUSTMENTS | [5 empty] | 4000 | 0.9 | [6 empty] | 4
Number of Portable / Local Air filter unit(s) in a room = |  | 0 | 1 | 1 | 1 | User defined | [8 empty] | 5
Air flow rate (CFM) per Portable / Local Air filter unit = |  | 400 | 400 | 400 | 400 | User defined | UVC Intensity (PORTABLE) | [7 empty] | 6
Portable Unit Runtime (Hr) |  | 6 | 6 | 6 | 6 | User defined | No UV-C | 0 | [6 empty] | 7
Portable air cleaners - Filter rating efficiency = |  | HEPA | HEPA | HEPA | HEPA | User Defined Filter efficiency based on particle size 0.1 µm. | UV-C | 0.7 | [6 empty] | 8
Portable air cleaners - UV-C option = |  | UV-C | UV-C | UV-C | UV-C | User Defined (*if portable has UV-C to kill influenza with min. 1200 dose (µ-watt-s/cm2), assumed 90% efficiency) | [8 empty] | 9
10
Pulmonary ventilation rate of a person m3/hr, ps = |  | 0.49271 | 0.49271 | 0.49271 | 0.49271 | Conversion to m3/hr from cfm (*1.699) | [8 empty] | 11
Room Area in m2, A = |  | 139.5 | 139.5 | 139.5 | 139.5 | Conversion to m2 from ft2 (*0.093) | [8 empty] | 12
Room Volume in m3, V = |  | 382.05 | 382.05 | 382.05 | 382.05 | Conversion to m3 from ft3 (*0.0283) | [8 empty] | 13
Ventilation air volume in m3/hr, Q(OA) = |  | 850.3401 | 850.3401 | 850.3401 | 850.3401 | Conversion to m3/hr from CFM (/0.588) | [8 empty] | 14
Recirculation air volume in m3/hr, Q(RA) = |  | 2551.0204 | 2551.0204 | 2551.0204 | 2551.0204 | Conversion to m3/hr from CFM (/0.588) | [8 empty] | 15
Air filter rating efficiency = |  | 0.2 | 0.2 | 0.2 | 0.55 | filter rating efficiency from table | [8 empty] | 16
pIQ/V |  | 0.083827 | 0.083827 | 0.083827 | 0.083827 | Calculated | [8 empty] | 17
e-ct |  | 1.086e-11 | 1.086e-11 | 1.086e-11 | 8.8328e-18 | Calculated | MERV RATING (BUILDING) |  | CFM/PERSON | TOTAL AIR |  | MERV RATING (PORTABLE) |  |  | 18
ct+e-ct-1/c2 |  | 1.3695 | 1.3695 | 1.3695 | 0.89343 | Calculated | [8 empty] | 19
Air disinfection UV-C intensity (µ-watt-s/cm2)= |  | 0% | 0% | 0% | 0% | UV C Dose in percentage | No Filter | 0 | 0 | 0 |  | No Filter | 0 |  | 20
PORTABLE | [6 empty] | MERV 6 | 0.1 | 1 | 1 |  | MERV 6 | 0.1 |  | 21
ct+e-ct-1/c2 |  | 1.3695 | 0.39841 | 0.39841 | 0.3449 |  | MERV 7 | 0.15 | 2 | 2 |  | MERV 7 | 0.15 |  | 22
Infectious particle removal rate by filtration, Kfiltration (/hr) = |  | 1.3354 | 12.0189 | 12.0189 | 14.356 | Calculated | MERV 8 | 0.2 | 3 | 3 |  | MERV 8 | 0.2 |  | 23
Total loss rate, C (/hr) = |  | 4.2077 | 14.8912 | 14.8912 | 17.2282 | Calculated | MERV 9 | 0.35 | 4 | 4 |  | MERV 9 | 0.35 |  | 24
Recirculation air volume in m3/hr, Q(RA) = (PORTABLE) |  | 0 | 680.2721 | 680.2721 | 680.2721 | Conversion to m3/hr from CFM (/0.588) | MERV 10 | 0.4 | 5 | 5 |  | MERV 10 | 0.4
Air filter rating Efficiency = (PORTABLE) |  | 0.95 | 0.95 | 0.95 | 0.95 | filter rating efficiency from table | MERV 11 | 0.45 | 6 | 6 |  | MERV 11 | 0.45
Air disinfection UV-C intensity (µ-watt-s/cm2)= (PORTABLE) |  | 70% | 70% | 70% | 70% | UV C Dose in percentage | MERV 12 | 0.5 | 7 | 7 |  | MERV 12 | 0.5
Recirculation air volume, Q(RA) (CFM) = (PORTABLE) |  | 0 | 400 | 400 | 400 | PORTABLE AIR CFM | MERV 13 | 0.55 | 8 | 8 |  | MERV 13 | 0.55
[7 empty] | MERV 14 | 0.6 | 9 | 9 |  | MERV 14 | 0.6
[7 empty] | MERV 15 | 0.9 | 10 | 10 |  | MERV 15 | 0.9
Probability of infection, P(infection) |  | 10.85% | 3.285% | 3.285% | 2.85% | Calculated, Considering Air cleaning portable & Local air filtration system + IAQ improvements in HVAC Central System | MERV 16 | 0.95 | 11 |  |  | MERV 16 | 0.95
Probability of infection, P(persons) |  | 3 | 1 | 1 | 1 |  | HEPA | 0.99 | 12 |  |  | HEPA | 0.95
[6 empty] | * No independent studies to reference |  |  | 13
Utilize for engineering guidance prior to your professional engineer implementing changes to your HVAC systems. | [8 empty] | 14
We acknowledge masks are not part of this estimator and CDC guidelines for social distancing and masks should still be followed. | [8 empty] | 15
16
17
18
19
20

## Source
SETTY-5.3 Estimator ®
SOURCE
1 | Miller SL, Nazaroff WW, Jimenez JL, Boerstra A, Buonanno G, Dancer SJ, Kurnitski J, Marr LC, Morawska L, Noakes C. Transmission of SARS-CoV-2 by inhalation of respiratory aerosol in the Skagit Valley Chorale superspreading event. doi:10.1101/2020.06.15.20132027. PPR:PPR176651.
2 | van Doremalen N, Bushmaker T, Morris DH, et al. Aerosol and Surface Stability of SARS-CoV-2 as Compared with SARS-CoV-1. N Engl J Med. 2020;382(16):1564-1567. doi:10.1056/NEJMc2004973
3 | Fears AC, Klimstra WB, Duprex P, et al. Comparative dynamic aerosol efficiencies of three emergent coronaviruses and the unusual persistence of SARS-CoV-2 in aerosol suspensions.
4 | Diapouli E, Chaloulakou A, Koutrakis P. Estimating the concentration of indoor particles of outdoor origin: A review. Journal of the Air & Waste Management Association. 2013;63:1113–1129.
5 | Thatcher TL, Lai ACK, Moreno-Jackson R, Sextro RG, Nazaroff WW. Effects of room furnishings and air speed on particle deposition rates indoors. Atmospheric Environment. 2002;36:1811–1819.
6 | Buonanno G, Stabile L, Morawska L. Estimation of airborne viral emission: Quanta emission rate of SARS-CoV-2 for infection risk assessment. Environ Int. 2020;141:105794. doi:10.1016/j.envint.2020.105794
7 | Buonanno, Giorgio & Morawska, Lidia & Stabile, Luca. (2020). Quantitative assessment of the risk of airborne transmission of SARS-CoV-2 infection: prospective and retrospective applications. 10.1101/2020.06.01.20118984.
8 | Gammaitoni, L. and Nucci, M.C. (1997a) Using a mathematical model to evaluate the efficacy of TB control measures, Emerg. Infect. Dis., 3, 335–342
9 | ASHRAE. ANSI/ASHRAE Standard 62.1-2016 Ventilation for Acceptable Indoor Air Quality.
10 | Hecker, R., Hofacre, K.C., 2008. Development of Performance Data for Common Building Air Cleaning Devices (Final Report No. EPA/600/R-08/013). U.S. Environmental Protection Agency, Office of Research and Development/National Homeland Security Centre Research Triangle Park, NC. Research Virions (or "particles") of corona viruses are spherical particles between 0.06 micron and 0.14 micron in diameter, averaging about 0.125 micron, measured by electron microscope (Zhu et al, 2020).
11 | IES Committee Report CR-2-20-V1, IES Photobiology Committee
12 | Contact tracing during Phase I of the COVID-19 pandemic in the Province of Trento, Italy: key ﬁndings and recommendations Pirous Fateh-Moghadam (1), Laura Bas (1), Silvia Molinaro (2), Steno Fontanari (3), Gabriele Dallago (3), Nancy Binkin (4), Mariagrazia Zuccali (2)
13 | COVID-19 in schools and early childhood education and care services – the Term 2 experience in NSW Prepared by the National Centre for Immunisation Research and Surveillance (NCIRS) 7/31/2020
14 | Identification of SAR-Cov-2 RNA in healthcare heating, Ventilation, and Air Conditioning Systems Patrick F. Horve1,*, Leslie Dietz1, Mark Fretz2, David A. Constant3, Andrew Wilkes4, John M. Townes5, Robert G. Martindale6, William B. Messer3, Kevin G. Van Den Wymelenberg1,2,*
15 | Contact tracing during coronavirus Disease Outbreak, South Korea, 2020 volume 26
16 | Controlling CDI, environmental services by Minnesota Hospital Association
17 | ASHRAE one hour UVGI course by William P Bahnfleth 04-21-2020
18 | The environmental control of epidemic contagion an epidemiologic study of radiant disinfection of air in day schools by W.F. Wells, M.W. Wells & T.S Wilder
19 | health.ny.gov/professionals/ems/pdf/assmttools.pdf
20 | ASHRAE.ORG
21 | ASHRAE STANDARD 170, VENTILATION OF HEALTHCARE FACILTIES
22 | OSSE Guidance Health and Safety Guidance for Schools 07.06.20
23 | 08-NIOSH-2003-136
24 | Minimum Classroom Size and Number of Students Per Classroom: C. Kenneth Tanner The University of Georgia School Design and Planning Laboratory April, 2000
25 | Portable cleaner refered model: https://www.blueair.com/us/air-purifiers/classic-205/1598.html